## Quick Zone
DSEAR Quick Zone |  |  | Gas and vapour zoning to IEC 60079-10-1
Pick a substance and an activity, then enter the amount. Yellow cells are inputs; everything else updates as you type.
1. What you’re handling |  |  | Result
Substance | Toluene | Add more on the Substances sheet | Zone 0, Zone 1 and Zone 2
Amount | 25 | litres handled in one go | Toluene · 25 litres · decanting / filling / sampling · indoors
Activity | Decanting / filling / sampling | Sets which sources of release exist | Zone | Extent from the activity |  | Equipment (EPL)
Indoor or outdoor | Indoor |  | Zone 0 | Inside the container |  | Ga
Temperature (°C) | 20 | Of the liquid or gas |  | Vapour space inside the receiving container.
Gas pressure (barg) | 10 | Gases only | Zone 1 | 0.52 m |  | Gb
Room volume (m³) | 100 | Indoors only |  | Vapour pushed out of the container mouth while filling. Limited by the amount handled.
Air changes per hour | 3 | 1 natural, 3–6 mechanical, 10+ LEV | Zone 2 | 2.65 m |  | Gc
Ventilation availability | Good | Fair or poor if it can fail |  | Spill of the full amount.
Air changes if ventilation fails | 0.5 | Closed building: about 0.25–1 | Equipment | Gas group IIA · temperature class T1 or better · AIT 480 °C
2. Assumptions |  |  | Plan view
Spill depth (mm) | 5 | Amount ÷ depth = pool area
Bund or drip-tray area (m²) |  | Optional. Caps the spill area
Container mouth while filling (m²) | 0.01 | 0.01 m² is about 110 mm across
Open surface: vessel, tin or tray (m²) | 0.1 | 0.1 m² is about 360 mm across
Wet area: rag and wiped surface (m²) | 0.2 | Rags activity only
Filling or charging rate (L/min) | 20 | Pushes vapour out of the opening
Air speed over liquid, indoors (m/s) | 0.3
Air speed over liquid, outdoors (m/s) | 0.5
Ventilation efficiency f, indoors | 2 | 1 perfect mixing, 5 very poor
Ventilation efficiency f, outdoors | 1
Gas leak hole area (mm²) | 0.25 | Small flange or valve, IEC Table B.1
Discharge coefficient Cd | 0.75
Flash point margin (°C) | 5 | This far below flash point: no zone
Safety factor k on LFL | 0.25 / 0.25 / 0.50 | Cont. / primary / secondary, on Tables
Looking down on the point of activity. Rings are drawn to scale; the spoke shows metres.
3. How each zone is sized
Grade of release | Source of release |  | Release (g/s) | Ventilation | Vz used (m³) | Zone (IEC Table D.1)
Continuous | Vapour space inside the receiving container |  | – | – | – | Zone 0 inside only
Primary | Vapour pushed out of the container mouth while filling |  | 0.037312 | Medium | 0.29218 | Zone 1
Secondary | Spill of the full amount |  | 0.31249 | Medium | 39.1528 | Zone 2
4. Compare activities
Activity | Zone 0 |  | Zone 1 |  | Zone 2 |  | Highest EPL
Closed containers / sealed system | Inside the containers |  | None |  | 2.65 m |  | Ga
Decanting / filling / sampling | Inside the container |  | 0.52 m |  | 2.65 m |  | Ga
Open vessel / continuous emission | Inside + 0.91 m |  | Within Zone 0 |  | 2.65 m |  | Ga
Open tin or tray | Inside + 0.91 m |  | None |  | 2.65 m |  | Ga
Wiping with solvent rags | Inside the solvent container |  | 1.14 m |  | 2.65 m |  | Ga
5. Notes
• Heavier than air: extend each zone down to the floor, the same distance across it, and into pits, drains and trenches. • Some releases are limited by the amount handled in one go. If the job repeats back to back, enter the amount per hour instead. • Distances are exact, with the safety factor k on the LFL. Final extents still need judgement on release direction, obstructions and openings.
This sheet supports, and does not replace, a competent-person DSEAR assessment. Check substance data against the SDS.
See the workings on the Quick Zone Calc sheet |  |  | Multiple sources or unusual releases: use the Gas-Vapour sheet

## Read Me
DSEAR Zoning Calculator
A screening tool for hazardous area classification under DSEAR. Gas and vapour zoning follows IEC 60079-10-1: release rate, hypothetical volume Vz, degree and availability of ventilation, then the zone, EPL, gas group and T-class. Dust zoning follows IEC 60079-10-2.
Sheets
Quick Zone: pick a substance, an activity and an amount, and get the Zone 0, 1 and 2 extents with a plan view.
Gas-Vapour: one row per source of release, up to 50 rows. Yellow is input, grey is from the library and green is a result.
Dust: one row per dust source, up to 40 rows.
Substances and Dusts: material property libraries. Add rows to extend the dropdowns.
Tables: constants, k factors, the zone matrix and the T-class table used by every formula.
Quick Zone Calc: the workings behind Quick Zone, source by source.
Why some activities have three zones
Each source of release has one grade. A continuous grade gives Zone 0, a primary grade gives Zone 1 and a secondary grade gives Zone 2. One activity can involve several sources at once, and their zones nest inside each other.
Decanting, filling and sampling have all three. The vapour space inside the receiving container is continuous (Zone 0), vapour pushed out of the container mouth while filling is primary (Zone 1), and a spill of the full amount is secondary (Zone 2).
An open vessel also has all three: the open liquid surface (Zone 0), charging the vessel (Zone 1), and a spill or overflow (Zone 2).
An open tin or tray left open is a continuous source (Zone 0) with a spill as its secondary source (Zone 2). Wiping with solvent rags has the vapour inside the solvent container (Zone 0), evaporation from the wet rag and the wiped surface (Zone 1), and a spill (Zone 2).
Closed containers have no release in normal operation, so there is no Zone 1. The inside of the containers is Zone 0 when the liquid is above its flash point, and outside there is only Zone 2 from a leak or spill.
A zone also drops out when ventilation dilutes its source to negligible extent, when a liquid is handled more than the flash point margin below its flash point, or when the substance is a gas, because a gas system holds no air.
Where ventilation availability is fair or poor, IEC Table D.1 adds an outer zone sized with the failed-ventilation rate. A zone only shows beyond the zone inside it where its own source reaches further; otherwise it is reported as within the inner zone.
Zone distances
Each distance is the exact radius of a hemisphere of volume Vz, with no rounding and no minimum distance. The safety factor is the IEC k on the LFL: 0.25 for continuous and primary grades and 0.5 for secondary, set on the Tables sheet. Zones with Vz under 0.1 m³ are negligible extent (NE).
The amount limits every release. A release cannot make more flammable mixture than the vapour its amount can give, so Vz used is the smaller of the steady Vz and that vapour divided by k × LFL. Enter the amount handled in one go, or the amount per hour if the job repeats back to back.
Quick Zone release rates
Spill (secondary): pool evaporation over amount ÷ spill depth, capped by any bund area.
Filling a container (primary): filling rate × saturated vapour density, plus evaporation from the container mouth.
Open liquid surface (continuous): pool evaporation over the vessel’s liquid surface.
Charging an open vessel (primary): filling rate × saturated vapour density, plus evaporation from the surface.
Wiping with rags (primary): evaporation from the wet area of the rag and the wiped surface.
Gases: every source uses the leak through the hole area at the stated pressure.
Saturated vapour density = pv × M / (R × T).
Gas and vapour method
1. Release rate dG/dt (kg/s)
Gas, choked (p > pc): W = Cd·S·p·√[ γ·M/(Z·R·T) · (2/(γ+1))^((γ+1)/(γ−1)) ]
Gas, subsonic: W = Cd·S·p·√[ M/(Z·R·T) · 2γ/(γ−1) · (1 − (pa/p)^((γ−1)/γ)) · (pa/p)^(2/γ) ]
Critical pressure: pc = pa·((γ+1)/2)^(γ/(γ−1))
Liquid jet: WL = Cd·S·√(2ρΔp); vapour rate = WL × vaporised fraction
Pool evaporation: We = 6.55·uw^0.78·Ap·pv·M^0.667 / (R·T), with pv in kPa
Vapour pressure: override cell, else Antoine log10(P/mmHg) = A − B/(C+T), else Trouton: pv = 101.325·exp(10.58·(1 − Tb/T))
2. Minimum ventilation flow (dV/dt)min = dG/dt / (k·LELm) × Ta/293, with LELm = 0.416×10⁻³ × M × LEL (vol%). k = 0.25 for continuous and primary grades, 0.5 for secondary.
3. Hypothetical volume Vz = f·(dV/dt)min / C, with C = ACH/3600 indoors and 0.03 s⁻¹ outdoors.
4. Degree of ventilation: high if Vz < 0.1 m³. Indoors, medium if Vz < V0 and low if Vz ≥ V0. Outdoors, medium otherwise.
5. Persistence time t = −(f/C)·ln(k·LEL/X0), with X0 = 100 vol%.
6. Zone from grade × degree × availability (Tables sheet). EPL Ga, Gb or Gc follows from the zone, and the T-class from the AIT.
Dust method
Zone from release: continuous gives Zone 20, primary Zone 21 and secondary Zone 22. Zone from layers: poor housekeeping gives Zone 21, fair Zone 22 and good none. The more onerous governs. Maximum surface temperature = min(⅔·MIT cloud, MIT 5 mm layer − 75 K).
Substance data
Library values are indicative, from standard references. White spirit is a mixture: its vapour pressure uses n-nonane Antoine constants as a surrogate and its boiling point is the start of the range. Check flash point, LFL, AIT and gas group against the SDS or IEC 60079-20-1 before relying on a result.
Limitations: read before use
• Vz measures ventilation effectiveness, not the zone extent. The radius is indicative only, so set final extents by judgement: jet direction, obstructions, heavier-than-air spread, pits and drains.
• The pool equation is not valid for liquids at or above their boiling point. Flashing releases need two-phase treatment.
• Hole sizes should follow IEC 60079-10-1 Table B.1 for the item and grade of release.
• Quick Zone release bases (filling rate, mouth area, open surface, wet area) are screening assumptions. Change them to match the actual task.
• This workbook supports, and does not replace, a competent-person DSEAR assessment.

## Gas-Vapour
Gas and vapour sources: IEC 60079-10-1 hypothetical volume (Vz) method
One row per source of release. Fill the yellow cells; grey cells come from the Substances sheet and green cells are results. Example rows 8 to 11 show the expected format, so overwrite or clear them.
Vz is not the zone extent: the radius is an indicative size only. Final zone extents need assessor judgement (release direction, obstructions, heavier-than-air spread). See the Read Me sheet for equations and limitations.
| Input |  | From library |  | Calculation |  | Result
Inputs: source of release | [19 empty] | Substance data | [8 empty] | Release rate | [7 empty] | Ventilation and zone
Ref | Source of release / location | Substance | Release type | Grade of release | Indoor / Outdoor | Pressure (barg) | Process / liquid temp (°C) | Ambient temp (°C) | Hole area S (mm²) | Discharge coeff. Cd | Compress-ibility Z | Vaporised fraction (liquid jet, blank = auto) | Pool area (m²) | Air velocity over pool (m/s) | Vapour pressure override (kPa) | Room volume V0 (m³) | Air changes per hour | Ventilation efficiency f (1–5) | Availability of ventilation | M (kg/kmol) | LFL (vol%) | γ | Liquid density (kg/m³) | Boiling point (°C) | Flash point (°C) | AIT (°C) | Gas group | Rel. vapour density (air = 1) | Pressure p (Pa abs) | Process temp T (K) | Ambient temp Ta (K) | Critical pressure pc (Pa abs) | Gas flow regime | Vapour pressure pv (kPa) | Liquid discharge (kg/s) | Vapour release rate dG/dt (kg/s) | LELm (kg/m³) | k | (dV/dt)min (m³/s) | Air changes C (s⁻¹) | Hypothetical volume Vz (m³) | Degree of ventilation | Persistence time t (min) | ZONE | Indicative radius, hemisphere of Vz (m) | Required EPL | Min. equipment group / T-class | Flags / notes
G1 | Propane line flange, LPG compound | Propane | Gas/vapour jet | Secondary | Outdoor | 10 | 20 | 20 | 2.5 | 0.75 | 1 | [6 empty] | 1 | Good | 44.1 | 1.7 | 1.13 | 493 | -42.1 |  | 450 | IIA | 1.5228 | 1101325 | 293.15 | 293.15 | 175165.1956 | Choked | n/a | n/a | 0.005574 | 0.031188 | 0.5 | 0.35764 | 0.03 | 11.9212 | Medium | 2.6487 | Zone 2 | 1.7855 | Gc | IIA T2 | Heavier than air — extend zone at low level / into pits and drains.
G2 | Natural gas regulator flange, boiler house | Methane | Gas/vapour jet | Secondary | Indoor | 2 | 20 | 20 | 1 | 0.75 | 1 |  |  |  |  | 200 | 3 | 2 | Fair | 16.04 | 4.4 | 1.31 |  | -161.5 |  | 600 | IIA | 0.55387 | 301325 | 293.15 | 293.15 | 186284.176 | Choked | n/a | n/a | 0.0003879 | 0.02936 | 0.5 | 0.026437 | 0.00083333 | 63.4496 | Medium | 152.6685 | Zone 2 | 3.1174 | Gc | IIA T1
L1 | Toluene drum decanting, spill to bund, solvent store | Toluene | Pool evaporation | Primary | Indoor |  | 20 | 20 |  |  |  |  | 1 | 0.3 |  | 500 | 6 | 2 | Good | 92.14 | 1 |  | 867 | 110.6 | 4 | 480 | IIA | 3.1816 | 101325 | 293.15 | 293.15 | n/a | n/a | 2.9113 | n/a | 6.2499e-05 | 0.03833 | 0.25 | 0.0065255 | 0.0016667 | 7.8306 | Medium | 119.8293 | Zone 1 | 1.5521 | Gb | IIA T1 | Heavier than air — extend zone at low level / into pits and drains.
L2 | LPG (butane) liquid pump seal, flashing release | n-Butane | Liquid jet | Secondary | Outdoor | 3 | 20 | 20 | 0.25 | 0.75 | [7 empty] | 1 | Good | 58.12 | 1.4 | 1.1 | 579 | -0.5 |  | 372 | IIA | 2.0069 | 401325 | 293.15 | 293.15 | n/a | n/a | 101.325 | 0.0034948 | 0.0034948 | 0.033849 | 0.5 | 0.2066 | 0.03 | 6.8865 | Medium | 2.7566 | Zone 2 | 1.487 | Gc | IIA T2 | Heavier than air — extend zone at low level / into pits and drains.
Note on J7: Equivalent leak hole cross-section. Use IEC 60079-10-1 Table B.1 for typical values by item and grade.
Note on K7: 0.50–0.75 sharp-edged orifice; 0.95–0.99 rounded. 0.75 is a common default.
Note on L7: Compressibility factor; 1.0 for ideal gas at modest pressure.
Note on M7: Fraction of a liquid jet that vaporises. Blank = 1 if at/above boiling point, else 0 (model the pool separately).
Note on O7: Air velocity over the pool surface. Indoors typically 0.1–0.5 m/s.
Note on P7: Leave blank to use Antoine constants (or Trouton estimate) from the Substances sheet.
Note on S7: 1 = uniform mixing; 1.5 mildly inefficient; up to 5 very inefficient (IEC 60079-10-1).
Note on AO7: Indoor: air changes per hour / 3600. Outdoor: fixed 0.03 s⁻¹ (Tables sheet).
Note on AQ7: High: Vz < 0.1 m³. Indoor Medium: Vz < V0; Low: Vz ≥ V0. Outdoor: Medium unless Vz < 0.1 m³.
Note on AR7: Time for concentration to fall from X0 to k×LFL after release stops: t = −(f/C)·ln(k·LFL/X0).
Note on AT7: Radius of a hemisphere with volume Vz. Indicative only — Vz is not the zone extent.

## Dust
Combustible dust: IEC 60079-10-2, surface temperatures per IEC 60079-14
Add dust properties on the Dusts sheet first. Zone extent is an assessor input: 1 m is a common starting point for Zone 21 or 22 around a source, adjusted for the dust and the release.
Ref | Source of release / location | Dust | Grade of release (dust cloud) | Housekeeping (dust layers) | Max layer thickness (mm) | Zone extent from source (m) | Dust group | MIT cloud (°C) | MIT 5 mm layer (°C) | MIE (mJ) | Zone from release | Zone from layers | ZONE | Required EPL | Cloud limit ⅔ × MIT (°C) | Layer limit (°C) | Max equipment surface temp (°C) | Flags / notes
D1 | Bag tipping station, mixing room | EXAMPLE organic dust | Primary | Fair | 2 | 1 | IIIB | 430 | 300 | 30 | 21 | 22 | Zone 21 | Db | 286.6667 | 225 | 225
Note on E5: Good: layers kept negligible → no zone from layers. Fair: layers present but removed before hazardous → Zone 22. Poor: layers persist → Zone 21 (IEC 60079-10-2).
Note on Q5: For layers up to 5 mm: MIT(5 mm layer) − 75 K. Thicker layers need the reduction graph in IEC 60079-14 or laboratory testing.

## Substances
Substance | Phase | Molar mass M (kg/kmol) | LFL (vol%) | UFL (vol%) | Polytropic index γ | Liquid density (kg/m³) | Boiling point (°C) | Flash point (°C) | Auto-ignition temp (°C) | Gas group | Antoine A | Antoine B | Antoine C | Notes | How to use
Methane | Gas | 16.04 | 4.4 | 17 | 1.31 |  | -161.5 |  | 600 | IIA |  |  |  | Indicative: check against the SDS or IEC 60079-20-1 | Add new materials in the empty rows (up to row 60); they appear automatically in the Gas-Vapour and Quick Zone dropdowns. γ is needed for gas jets; liquid density for liquid jets; boiling point for pool/flash checks. Antoine constants are log10(P/mmHg) = A − B/(C + T/°C), from standard tables (Lange's Handbook); if blank, vapour pressure is estimated from the boiling point using Trouton's rule, or enter it directly on the calculator. Where sources disagree, the lower AIT / higher gas group has been used.
Propane | Gas | 44.1 | 1.7 | 10.9 | 1.13 | 493 | -42.1 |  | 450 | IIA |  |  |  | Indicative: check against the SDS or IEC 60079-20-1
n-Butane | Gas | 58.12 | 1.4 | 9.3 | 1.1 | 579 | -0.5 |  | 372 | IIA |  |  |  | Indicative: check against the SDS or IEC 60079-20-1
Hydrogen | Gas | 2.016 | 4 | 77 | 1.41 |  | -252.9 |  | 560 | IIC |  |  |  | Indicative: check against the SDS or IEC 60079-20-1
Ethylene | Gas | 28.05 | 2.3 | 36 | 1.24 |  | -103.7 |  | 440 | IIB |  |  |  | Indicative: check against the SDS or IEC 60079-20-1
Acetylene | Gas | 26.04 | 2.3 | 100 | 1.23 |  | -84 |  | 305 | IIC |  |  |  | Indicative: check against the SDS or IEC 60079-20-1
Ammonia | Gas | 17.03 | 15 | 33.6 | 1.31 |  | -33.3 |  | 630 | IIA |  |  |  | Indicative: check against the SDS or IEC 60079-20-1
Hydrogen sulphide | Gas | 34.08 | 4 | 45.5 | 1.32 |  | -60.3 |  | 260 | IIB |  |  |  | Indicative: check against the SDS or IEC 60079-20-1
Methanol | Liquid | 32.04 | 6 | 36 |  | 791 | 64.7 | 11 | 440 | IIA | 8.081 | 1582.271 | 239.726 | Indicative: check against the SDS or IEC 60079-20-1
Ethanol | Liquid | 46.07 | 3.1 | 19 |  | 789 | 78.4 | 13 | 363 | IIB | 8.2042 | 1642.89 | 230.3 | Indicative: check against the SDS or IEC 60079-20-1
Isopropanol (IPA) | Liquid | 60.1 | 2 | 12.7 |  | 786 | 82.3 | 12 | 399 | IIA | 8.1178 | 1580.92 | 219.61 | Indicative: check against the SDS or IEC 60079-20-1
Acetone | Liquid | 58.08 | 2.5 | 13 |  | 784 | 56.1 | -18 | 465 | IIA | 7.1171 | 1210.595 | 229.664 | Indicative: check against the SDS or IEC 60079-20-1
Ethyl acetate | Liquid | 88.11 | 2 | 11.5 |  | 902 | 77.1 | -4 | 426 | IIA | 7.1018 | 1244.95 | 217.88 | Indicative: check against the SDS or IEC 60079-20-1
Toluene | Liquid | 92.14 | 1 | 7.1 |  | 867 | 110.6 | 4 | 480 | IIA | 6.9546 | 1344.8 | 219.482 | Indicative: check against the SDS or IEC 60079-20-1
Xylene (mixed) | Liquid | 106.17 | 1 | 7 |  | 864 | 138 | 25 | 464 | IIA | 6.9905 | 1453.43 | 215.31 | Indicative: check against the SDS or IEC 60079-20-1
n-Hexane | Liquid | 86.18 | 1 | 7.5 |  | 659 | 68.7 | -22 | 225 | IIA | 6.876 | 1171.17 | 224.41 | Indicative: check against the SDS or IEC 60079-20-1
n-Heptane | Liquid | 100.2 | 1.1 | 6.7 |  | 684 | 98.4 | -4 | 204 | IIA | 6.8938 | 1264.37 | 216.636 | Indicative: check against the SDS or IEC 60079-20-1
Diethyl ether | Liquid | 74.12 | 1.7 | 36 |  | 713 | 34.6 | -45 | 160 | IIB | 6.9203 | 1064.07 | 228.8 | Indicative: check against the SDS or IEC 60079-20-1
White spirit | Liquid | 140 | 0.6 | 6.5 |  | 785 | 150 | 38 | 240 | IIA | 6.9389 | 1431.82 | 202.01 | Mixture (BS 245 regular grade). n-Nonane Antoine as a surrogate. Check the SDS for your grade.

## Dusts
Dust | Dust group | MIT cloud (°C) | MIT 5 mm layer (°C) | MIE (mJ) | Kst (bar·m/s) | Notes | Use laboratory data (e.g. from the dust's test report or GESTIS-DUST-EX). Group: IIIA combustible flyings, IIIB non-conductive dust, IIIC conductive dust.
EXAMPLE organic dust | IIIB | 430 | 300 | 30 | 150 | Placeholder values: replace with test data for your material

## Tables
Constants and lookup tables
Edit with care: every sheet reads from here.
Constant | Value | Basis
Atmospheric pressure pa (Pa) | 101325 | IEC 60079-10-1 reference conditions
Universal gas constant R (J/kmol·K) | 8314
Initial concentration X0 for persistence time (vol%) | 100 | IEC 60079-10-1:2008 Annex B (pure release)
Vz threshold for HIGH degree of ventilation (m³) | 0.1 | Vz below this is treated as negligible (2008 Annex B)
Outdoor air change rate C (s⁻¹) | 0.03 | 2008 Annex B: outdoor, ~0.5 m/s wind through a notional 15 m cube
Reference temperature (K) | 293 | Used in (dV/dt)min temperature correction
LELm conversion factor (kg/m³ per kg/kmol per vol%) | 0.000416 | LELm = 0.416×10⁻³ × M × LEL(vol%)
Outdoor calm-wind factor (fraction of normal C) | 0.5 | Quick Zone outer zone sizing outdoors: C2 = 0.03 × factor (assessor assumption)
Room height for the Quick Zone plan view (m) | 3 | Plan view only: a whole-room zone is drawn as a disc the size of the room floor
Safety factor k on LEL
Grade | k
Continuous | 0.25 | IEC 60079-10-1:2008: k = 0.25 continuous/primary, 0.5 secondary
Primary | 0.25
Secondary | 0.5
Zone from grade of release, degree and availability of ventilation (IEC 60079-10-1 Table B.1 / D.1)
Grade \ Degree-Availability | High-Good | High-Fair | High-Poor | Medium-Good | Medium-Fair | Medium-Poor | Low-Good | Low-Fair | Low-Poor
Continuous | Non-hazardous (Zone 0 NE) | Zone 2 (Zone 0 NE) | Zone 1 (Zone 0 NE) | Zone 0 | Zone 0 + Zone 2 | Zone 0 + Zone 1 | Zone 0 | Zone 0 | Zone 0
Primary | Non-hazardous (Zone 1 NE) | Zone 2 (Zone 1 NE) | Zone 2 (Zone 1 NE) | Zone 1 | Zone 1 + Zone 2 | Zone 1 + Zone 2 | Zone 1 or Zone 0 | Zone 1 or Zone 0 | Zone 1 or Zone 0
Secondary | Non-hazardous (Zone 2 NE) | Non-hazardous (Zone 2 NE) | Zone 2 | Zone 2 | Zone 2 | Zone 2 | Zone 1 and even Zone 0 | Zone 1 and even Zone 0 | Zone 1 and even Zone 0
Notes: 'NE' = zone of negligible extent. 'Zone 1 or Zone 0' (low dilution, primary) is Zone 0 if ventilation is so weak that the release is effectively continuous. Low-dilution secondary: Zone 1 and possibly Zone 0, by assessor judgement.
Temperature class from auto-ignition temperature
AIT above (°C) | T-class | Max surface temp (°C)
0 | T6 or lower: check | 85
85 | T6 | 85
100 | T5 | 100
135 | T4 | 135
200 | T3 | 200
300 | T2 | 300
450 | T1 | 450
Equipment T-class maximum surface temperature must be below the AIT (IEC 60079-14).
Quick Zone activities and their sources of release
Activity | Continuous source (Zone 0) | Primary source (Zone 1) | Secondary source (Zone 2)
Closed containers / sealed system | Vapour space inside the containers | None: no release in normal operation | Leak or spill of the full amount
Decanting / filling / sampling | Vapour space inside the receiving container | Vapour pushed out of the container mouth while filling | Spill of the full amount
Open vessel / continuous emission | Evaporation from the open liquid surface | Vapour pushed out while charging the vessel | Spill or overflow of the full amount
Open tin or tray | Evaporation from the open liquid surface | None: no other release in normal operation | Spill of the full amount
Wiping with solvent rags | Vapour space inside the solvent container | Evaporation from the wet rag and the wiped surface | Spill of the full amount
Gases use the leak through the hole area for every source. There is no Zone 0 inside a gas system because it holds no air. Liquids handled below their flash point have no Zone 0 inside.

## Quick Zone Calc
Quick Zone Calc
The workings behind the Quick Zone sheet, source by source. Nothing here is an input: change values on Quick Zone or Tables.
1. Substance and conditions
Phase | Liquid | From the Substances sheet
Gas? | FALSE
Molar mass M | 92.14 | kg/kmol
LFL | 1 | vol%
Polytropic index γ |  | Gases only
Liquid density | 867 | kg/m³
Boiling point | 110.6 | °C
Flash point | 4 | °C
Auto-ignition temperature | 480 | °C
Gas group | IIA
Antoine A | 6.9546 | log10(P/mmHg) = A − B/(C + T)
Antoine B | 1344.8
Antoine C | 219.482
Temperature T | 293.15 | K
Vapour pressure pv | 2.9113 | kPa. Antoine, else Trouton from the boiling point
Saturated vapour concentration | 2.8732 | vol%. Above the LFL means flammable headspace
Saturated vapour density | 0.11006 | kg/m³ of vapour in the headspace
LELm | 0.03833 | kg/m³
Relative vapour density | 3.1816 | Air = 1
Heavier than air? | TRUE | Above 1.2
Outdoors? | FALSE
Ventilation efficiency f | 2
Air changes C, normal | 0.00083333 | s⁻¹
Air changes C, ventilation failed | 0.00013889 | s⁻¹. Outdoors: calm-wind factor on Tables
Air speed over the liquid | 0.3 | m/s
Below flash point minus margin? | FALSE | If TRUE, no zone is normally needed
At or above boiling point? | FALSE
Zone 0 inside containers? | TRUE | Liquid at or above its flash point less the margin
Temperature class | T1 | From the AIT
Room-equivalent radius | 3.2574 | m. Plan view of a whole-room zone
2. Release rates and the vapour each amount can give
Gas pressure p | n/a | Pa abs
Critical pressure pc | n/a | Pa abs
Gas leak through the hole | n/a | kg/s. Choked if p > pc, else subsonic
Evaporation per m² of liquid surface | 6.2499e-05 | kg/s per m². We = 6.55·u^0.78·A·pv·M^0.667/(R·T)
Spill pool area | 5 | m². Amount ÷ spill depth, capped by any bund
Vapour pushed out by filling | 3.6687e-05 | kg/s. Filling rate × saturated vapour density
Release: spill or leak | 0.00031249 | kg/s
Release: filling a container | 3.7312e-05 | kg/s. Displacement + evaporation at the mouth
Release: open liquid surface | 6.2499e-06 | kg/s
Release: charging an open vessel | 4.2937e-05 | kg/s. Displacement + evaporation at the surface
Release: wet rag and wiped surface | 1.25e-05 | kg/s
Vapour the whole amount can give | 21.675 | kg. All of the amount evaporates or leaks
Vapour from filling the amount | 0.0027984 | kg. Displaced vapour + mouth evaporation while filling
Vapour from charging the vessel | 0.0032203 | kg. Displaced vapour + surface evaporation while charging
Time to evaporate the spill or empty the system | 1156.023 | min
3. Sources of release, by activity
Activity | Grade | Source of release | Applies | Sized by Vz | Release dG/dt (kg/s) | Most vapour the amount can give (kg) | k | (dV/dt)min (m³/s) | Vz, steady (m³) | Vz limit from the amount (m³) | Vz used (m³) | Limited by the amount? | Degree of ventilation | IEC Table D.1 result | Inner zone | Inner zone NE? | Inner radius (m) | Outer zone | Vz, ventilation failed, steady (m³) | Vz, ventilation failed, used (m³) | Outer limited by amount? | Outer radius (m) | Persistence (min) | Low dilution? | To Zone 0 (m) | To Zone 1 (m) | To Zone 2 (m) | NE Zone 0 (m) | NE Zone 1 (m) | NE Zone 2 (m)
Closed containers / sealed system | Continuous | Vapour space inside the containers | TRUE | FALSE | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | 0
Closed containers / sealed system | Primary | No release in normal operation | FALSE | FALSE | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | –
Closed containers / sealed system | Secondary | Leak or spill of the full amount | TRUE | TRUE | 0.00031249 | 21.675 | 0.5 | 0.016314 | 39.1528 | 1131.5398 | 39.1528 | FALSE | Medium | Zone 2 | 2 | FALSE | 2.654 | – | 234.9171 | 234.9171 | FALSE | – | 211.9327 | FALSE |  |  | 2.654
Decanting / filling / sampling | Continuous | Vapour space inside the receiving container | TRUE | FALSE | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | 0
Decanting / filling / sampling | Primary | Vapour pushed out of the container mouth while filling | TRUE | TRUE | 3.7312e-05 | 0.0027984 | 0.25 | 0.0038958 | 9.3498 | 0.29218 | 0.29218 | TRUE | Medium | Zone 1 | 1 | FALSE | 0.51864 | – | 56.099 | 0.29218 | TRUE | – | 239.6586 | FALSE |  | 0.51864
Decanting / filling / sampling | Secondary | Spill of the full amount | TRUE | TRUE | 0.00031249 | 21.675 | 0.5 | 0.016314 | 39.1528 | 1131.5398 | 39.1528 | FALSE | Medium | Zone 2 | 2 | FALSE | 2.654 | – | 234.9171 | 234.9171 | FALSE | – | 211.9327 | FALSE |  |  | 2.654
Open vessel / continuous emission | Continuous | Evaporation from the open liquid surface | TRUE | TRUE | 6.2499e-06 | 21.675 | 0.25 | 0.00065255 | 1.5661 | 2263.0796 | 1.5661 | FALSE | Medium | Zone 0 | 0 | FALSE | 0.90766 | – | 9.3967 | 9.3967 | FALSE | – | 239.6586 | FALSE | 0.90766
Open vessel / continuous emission | Primary | Vapour pushed out while charging the vessel | TRUE | TRUE | 4.2937e-05 | 0.0032203 | 0.25 | 0.0044831 | 10.7593 | 0.33623 | 0.33623 | TRUE | Medium | Zone 1 | 1 | FALSE | 0.54349 | – | 64.556 | 0.33623 | TRUE | – | 239.6586 | FALSE |  | 0.54349
Open vessel / continuous emission | Secondary | Spill or overflow of the full amount | TRUE | TRUE | 0.00031249 | 21.675 | 0.5 | 0.016314 | 39.1528 | 1131.5398 | 39.1528 | FALSE | Medium | Zone 2 | 2 | FALSE | 2.654 | – | 234.9171 | 234.9171 | FALSE | – | 211.9327 | FALSE |  |  | 2.654
Open tin or tray | Continuous | Evaporation from the open liquid surface | TRUE | TRUE | 6.2499e-06 | 21.675 | 0.25 | 0.00065255 | 1.5661 | 2263.0796 | 1.5661 | FALSE | Medium | Zone 0 | 0 | FALSE | 0.90766 | – | 9.3967 | 9.3967 | FALSE | – | 239.6586 | FALSE | 0.90766
Open tin or tray | Primary | No other release in normal operation | FALSE | FALSE | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | –
Open tin or tray | Secondary | Spill of the full amount | TRUE | TRUE | 0.00031249 | 21.675 | 0.5 | 0.016314 | 39.1528 | 1131.5398 | 39.1528 | FALSE | Medium | Zone 2 | 2 | FALSE | 2.654 | – | 234.9171 | 234.9171 | FALSE | – | 211.9327 | FALSE |  |  | 2.654
Wiping with solvent rags | Continuous | Vapour space inside the solvent container | TRUE | FALSE | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | – | 0
Wiping with solvent rags | Primary | Evaporation from the wet rag and the wiped surface | TRUE | TRUE | 1.25e-05 | 21.675 | 0.25 | 0.0013051 | 3.1322 | 2263.0796 | 3.1322 | FALSE | Medium | Zone 1 | 1 | FALSE | 1.1436 | – | 18.7934 | 18.7934 | FALSE | – | 239.6586 | FALSE |  | 1.1436
Wiping with solvent rags | Secondary | Spill of the full amount | TRUE | TRUE | 0.00031249 | 21.675 | 0.5 | 0.016314 | 39.1528 | 1131.5398 | 39.1528 | FALSE | Medium | Zone 2 | 2 | FALSE | 2.654 | – | 234.9171 | 234.9171 | FALSE | – | 211.9327 | FALSE |  |  | 2.654
Radii are exact: the radius of a hemisphere of volume Vz, with no rounding and no minimum. Vz used is the smaller of the steady Vz and the most the amount can make at k × LFL. 9999 = whole room. "To Zone" columns carry the radius each source adds to that zone; NE columns carry zones of negligible extent (Vz under 0.1 m³).
4. Zoning regime, by activity
Activity | Zone 0 inside? | Zone 0 from sources (m) | Zone 1 from sources (m) | Zone 2 from sources (m) | Zone 0 NE (m) | Zone 1 NE (m) | Zone 2 NE (m) | Zone 0 (m) | Zone 1 (m) | Zone 2 (m) | Zone 0 extent | Zone 1 extent | Zone 2 extent | Zone 0 present | Zone 1 present | Zone 2 present | Headline | EPL Zone 0 | EPL Zone 1 | EPL Zone 2 | Largest finite radius (m) | Whole-room plot radius (m) | Plot Zone 0 (m) | Plot Zone 1 (m) | Plot Zone 2 (m) | Most onerous EPL | Low dilution? | Limited by the amount?
Closed containers / sealed system | TRUE | 0 | -1 | 2.654 | -1 | -1 | -1 | 0 | -1 | 2.654 | Inside the containers | None | 2.65 m | TRUE | FALSE | TRUE | Zone 0 and Zone 2 | Ga | – | Gc | 2.654 | 3.2574 | 0.3 | 0 | 2.654 | Ga | FALSE | FALSE
Decanting / filling / sampling | TRUE | 0 | 0.51864 | 2.654 | -1 | -1 | -1 | 0 | 0.51864 | 2.654 | Inside the container | 0.52 m | 2.65 m | TRUE | TRUE | TRUE | Zone 0, Zone 1 and Zone 2 | Ga | Gb | Gc | 2.654 | 3.2574 | 0.3 | 0.51864 | 2.654 | Ga | FALSE | TRUE
Open vessel / continuous emission | TRUE | 0.90766 | 0.54349 | 2.654 | -1 | -1 | -1 | 0.90766 | -3 | 2.654 | Inside + 0.91 m | Within Zone 0 | 2.65 m | TRUE | FALSE | TRUE | Zone 0 and Zone 2 | Ga | – | Gc | 2.654 | 3.2574 | 0.90766 | 0 | 2.654 | Ga | FALSE | TRUE
Open tin or tray | TRUE | 0.90766 | -1 | 2.654 | -1 | -1 | -1 | 0.90766 | -1 | 2.654 | Inside + 0.91 m | None | 2.65 m | TRUE | FALSE | TRUE | Zone 0 and Zone 2 | Ga | – | Gc | 2.654 | 3.2574 | 0.90766 | 0 | 2.654 | Ga | FALSE | FALSE
Wiping with solvent rags | TRUE | 0 | 1.1436 | 2.654 | -1 | -1 | -1 | 0 | 1.1436 | 2.654 | Inside the solvent container | 1.14 m | 2.65 m | TRUE | TRUE | TRUE | Zone 0, Zone 1 and Zone 2 | Ga | Gb | Gc | 2.654 | 3.2574 | 0.3 | 1.1436 | 2.654 | Ga | FALSE | FALSE
5. Selected activity (feeds the Quick Zone sheet)
Activity number | 2 | 1 closed, 2 decanting, 3 open vessel, 4 open tin, 5 rags
Headline | Zone 0, Zone 1 and Zone 2
Zone 0 extent (m) | 0 | -1 none, -2 in a whole-room zone, -3 inside the inner zone, 9999 whole room
Zone 1 extent (m) | 0.51864
Zone 2 extent (m) | 2.654
Zone 0 from sources (m) | 0
Zone 1 from sources (m) | 0.51864
Zone 2 from sources (m) | 2.654
Zone 0 negligible (m) | -1
Zone 1 negligible (m) | -1
Zone 2 negligible (m) | -1
Zone 0 extent | Inside the container
Zone 1 extent | 0.52 m
Zone 2 extent | 2.65 m
Zone 0 present? | TRUE
Zone 1 present? | TRUE
Zone 2 present? | TRUE
EPL in Zone 0 | Ga
EPL in Zone 1 | Gb
EPL in Zone 2 | Gc
Plot radius, Zone 0 (m) | 0.3
Plot radius, Zone 1 (m) | 0.51864
Plot radius, Zone 2 (m) | 2.654
Low dilution? | FALSE
Limited by the amount? | TRUE
Zone 0: source that sets it (1-3) | 1 | 1 continuous, 2 primary, 3 secondary
Zone 0: that source sized by Vz? | FALSE
Zone 0: set by failed ventilation? | FALSE
Zone 0: limited by the amount? | FALSE
Zone 0 basis | Vapour space inside the receiving container.
Zone 1: source that sets it (1-3) | 2 | 1 continuous, 2 primary, 3 secondary
Zone 1: that source sized by Vz? | TRUE
Zone 1: set by failed ventilation? | FALSE
Zone 1: limited by the amount? | TRUE
Zone 1 basis | Vapour pushed out of the container mouth while filling. Limited by the amount handled.
Zone 2: source that sets it (1-3) | 3 | 1 continuous, 2 primary, 3 secondary
Zone 2: that source sized by Vz? | TRUE
Zone 2: set by failed ventilation? | FALSE
Zone 2: limited by the amount? | FALSE
Zone 2 basis | Spill of the full amount.
Summary line | Toluene · 25 litres · decanting / filling / sampling · indoors
Equipment line | Gas group IIA · temperature class T1 or better · AIT 480 °C
Notes | • Heavier than air: extend each zone down to the floor, the same distance across it, and into pits, drains and trenches. • Some releases are limited by the amount handled in one go. If the job repeats back to back, enter the amount per hour instead. • Distances are exact, with the safety factor k on the LFL. Final extents still need judgement on release direction, obstructions and openings.
6. Plan view chart data
Bearing (°) | Zone 2 · 2.65 m | Zone 1 · 0.52 m | Zone 0 · inside the container | Point of activity
0 | 2.654 | 0.51864 | 0.3 | 0.07962
5 | 2.654 | 0.51864 | 0.3 | 0.07962
10 | 2.654 | 0.51864 | 0.3 | 0.07962
15 | 2.654 | 0.51864 | 0.3 | 0.07962
20 | 2.654 | 0.51864 | 0.3 | 0.07962
25 | 2.654 | 0.51864 | 0.3 | 0.07962
30 | 2.654 | 0.51864 | 0.3 | 0.07962
35 | 2.654 | 0.51864 | 0.3 | 0.07962
40 | 2.654 | 0.51864 | 0.3 | 0.07962
45 | 2.654 | 0.51864 | 0.3 | 0.07962
50 | 2.654 | 0.51864 | 0.3 | 0.07962
55 | 2.654 | 0.51864 | 0.3 | 0.07962
60 | 2.654 | 0.51864 | 0.3 | 0.07962
65 | 2.654 | 0.51864 | 0.3 | 0.07962
70 | 2.654 | 0.51864 | 0.3 | 0.07962
75 | 2.654 | 0.51864 | 0.3 | 0.07962
80 | 2.654 | 0.51864 | 0.3 | 0.07962
85 | 2.654 | 0.51864 | 0.3 | 0.07962
90 | 2.654 | 0.51864 | 0.3 | 0.07962
95 | 2.654 | 0.51864 | 0.3 | 0.07962
100 | 2.654 | 0.51864 | 0.3 | 0.07962
105 | 2.654 | 0.51864 | 0.3 | 0.07962
110 | 2.654 | 0.51864 | 0.3 | 0.07962
115 | 2.654 | 0.51864 | 0.3 | 0.07962
120 | 2.654 | 0.51864 | 0.3 | 0.07962
125 | 2.654 | 0.51864 | 0.3 | 0.07962
130 | 2.654 | 0.51864 | 0.3 | 0.07962
135 | 2.654 | 0.51864 | 0.3 | 0.07962
140 | 2.654 | 0.51864 | 0.3 | 0.07962
145 | 2.654 | 0.51864 | 0.3 | 0.07962
150 | 2.654 | 0.51864 | 0.3 | 0.07962
155 | 2.654 | 0.51864 | 0.3 | 0.07962
160 | 2.654 | 0.51864 | 0.3 | 0.07962
165 | 2.654 | 0.51864 | 0.3 | 0.07962
170 | 2.654 | 0.51864 | 0.3 | 0.07962
175 | 2.654 | 0.51864 | 0.3 | 0.07962
180 | 2.654 | 0.51864 | 0.3 | 0.07962
185 | 2.654 | 0.51864 | 0.3 | 0.07962
190 | 2.654 | 0.51864 | 0.3 | 0.07962
195 | 2.654 | 0.51864 | 0.3 | 0.07962
200 | 2.654 | 0.51864 | 0.3 | 0.07962
205 | 2.654 | 0.51864 | 0.3 | 0.07962
210 | 2.654 | 0.51864 | 0.3 | 0.07962
215 | 2.654 | 0.51864 | 0.3 | 0.07962
220 | 2.654 | 0.51864 | 0.3 | 0.07962
225 | 2.654 | 0.51864 | 0.3 | 0.07962
230 | 2.654 | 0.51864 | 0.3 | 0.07962
235 | 2.654 | 0.51864 | 0.3 | 0.07962
240 | 2.654 | 0.51864 | 0.3 | 0.07962
245 | 2.654 | 0.51864 | 0.3 | 0.07962
250 | 2.654 | 0.51864 | 0.3 | 0.07962
255 | 2.654 | 0.51864 | 0.3 | 0.07962
260 | 2.654 | 0.51864 | 0.3 | 0.07962
265 | 2.654 | 0.51864 | 0.3 | 0.07962
270 | 2.654 | 0.51864 | 0.3 | 0.07962
275 | 2.654 | 0.51864 | 0.3 | 0.07962
280 | 2.654 | 0.51864 | 0.3 | 0.07962
285 | 2.654 | 0.51864 | 0.3 | 0.07962
290 | 2.654 | 0.51864 | 0.3 | 0.07962
295 | 2.654 | 0.51864 | 0.3 | 0.07962
300 | 2.654 | 0.51864 | 0.3 | 0.07962
305 | 2.654 | 0.51864 | 0.3 | 0.07962
310 | 2.654 | 0.51864 | 0.3 | 0.07962
315 | 2.654 | 0.51864 | 0.3 | 0.07962
320 | 2.654 | 0.51864 | 0.3 | 0.07962
325 | 2.654 | 0.51864 | 0.3 | 0.07962
330 | 2.654 | 0.51864 | 0.3 | 0.07962
335 | 2.654 | 0.51864 | 0.3 | 0.07962
340 | 2.654 | 0.51864 | 0.3 | 0.07962
345 | 2.654 | 0.51864 | 0.3 | 0.07962
350 | 2.654 | 0.51864 | 0.3 | 0.07962
355 | 2.654 | 0.51864 | 0.3 | 0.07962